New Type AC Contactor LC1-D

1. GENERAL

- 1.1 Certificates: CE;

- 1.2 Electric ratings: AC50/60Hz, 690V, up to 620A ;

- 1.3 Application: remote making & breaking circuits, protect circuit from over-load when assembling with thermal over-load relay, frequent start-up and control of AC motor; .

- 1.4 Utilization category: AC-3, AC-4;

- 1.5 Altitude:≤2000m;

- 1.6 Ambient temperature: -5℃~ +40℃;

- 1.7 Mounting category: Ⅲ;

- 1.8 Mounting conditions: inclination between the mounting plane and the vertical plane should not exceed 士5° ;

- 1.9 Standard: IEC/EN 60947-4-1.

2.TECHNICAL DATA

| Items |  | Model | LC1-D09 | LC1-D12 | LC1-D18 | LC1-D25 | LC1-D32 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Pole |  |  | 3/4 | 3/4 | 3/4 | 3/4 | 3/4 |
| Auxiliary Contact |  |  | 1NO+1NC | 1NO+1NC | 1NO+1NC | 1NO+1NC | 1NO+1NC |
| Rated conventional heating current (A) AC-1 |  |  | 20 | 20 | 30 | 40 | 50 |
| Rated operational current (A) | 380/400V | AC-1 AC-4 | 9 | 12 | 18 | 25 | 32 |
|  |  |  | 3.5 | 5 | 7.7 | 8.5 | 12 |
|  | 660/690V | AC-3 AC-4 | 6.6 | 8.9 | 12 | 18 | 21 |
|  |  |  | 1.5 | 2 | 3.8 | 4.4 | 7.5 |
| Rated insulation voltage (V AC) |  |  | 690 | 690 | 690 | 690 | 690 |
| Power of controlled 3-phase cage motor (AC-3) | kW | 220/230V AC 380/415V AC 660/690V AC | 2.2 | 3 | 4 | 5.5 | 7.5 |
|  |  |  | 4 | 5.5 | 7.5 | 11 | 15 |
|  |  |  | 5.5 | 7.5 | 10 | 15 | 18.5 |
| AC coil(V) |  |  | 24，36，48，110，127，220，240，380，415，440，480，500，600 |  |  |  |  |
| DC coil(V) |  |  | 24，36，48，110，220 |  |  |  |  |

| Items |  | Model | LC1-D40 | LC1-D50 | LC1-D65 | LC1-D80 | LC1-D95 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Pole |  |  | 3/4 | 3/4 | 3/4 | 3/4 | 3/4 |
| Auxilirary Circuit Cat:AC-15,Ue=4 15V le=0.95A Ith=10A |  |  | 1NO+1NC | 1NO+1NC | 1NO+1NC | 1NO+1NC | 1NO+1NC |
| Rated conventional heating current (A) AC-1 |  |  | 60 | 80 | 80 | 110 | 110 |
| Rated operational current (A) | 380/400V | AC-3 AC-4 | 40 | 50 | 65 | 80 | 95 |
|  |  |  | 18.5 | 24 | 28 | 37 | 44 |
|  | 660/690V | AC-3 AC-4 | 34 | 39 | 42 | 49 | 49 |
|  |  |  | 9 | 12 | 14 | 17.3 | 21.3 |
| Rated insulation voltage (V AC) |  |  | 690 | 690 | 690 | 690 | 690 |
| Power of controlled 3-phase cage motor (AC-3) | KW | 220/230V AC 380/415V AC 660/690V AC | 11 | 15 | 18.5 | 22 | 25 |
|  |  |  | 18.5 | 22 | 30 | 37 | 45 |
|  |  |  | 30 | 37 | 37 | 45 | 45 |
| AC coil(V) |  |  | 24，36，48，110，127，220，240，380，415，440，480，500，600 |  |  |  |  |
| DC coil(V) |  |  | 24，36，48，110，220 |  |  |  |  |

| Items |  | Model | LC1-D115 | LC1-D150 | LC1-D170 | LC1-D205 | LC1-D245 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Pole |  |  | 3 | 3 | 3 | 3/4 | 3/4 |
| Rated conventional heating current (A) AC-1 |  |  | 200 | 200 | 200 | 275 | 280 |
| Rated operational current (A) | 380/400V | AC-3 AC-4 | 115 | 150 | 170 | 205 | 245 |
|  |  |  | 50 | 65 | 70 | 75 | 85 |
|  | 660/690V | AC-3 AC-4 | 70 | 90 | 100 | 108 | 115 |
|  |  |  | 25 | 32 | 35 | 38 | 40 |
| Rated insulation voltage (V AC) |  |  | 690 | 690 | 690 | 690 | 690 |
| Power of controlled 3-phase cage motor (AC-3) | kW | 380/415V AC 660/690V AC | 55 | 75 | 75 | 90 | 110 |
|  |  |  | 80 | 100 | 100 | 110 | 140 |
| AC coil(V) |  |  | 110，127，220，240，380，415，440，480，500，600 |  |  |  |  |

| Items |  | Model | LC1-D300 | LC1-D410 | LC1-D475 | LC1-D620 |
| --- | --- | --- | --- | --- | --- | --- |
| Pole |  |  | 3/4 | 3/4 | 3/4 | 3/4 |
| Rated conventional heating current (A) AC-1 |  |  | 360 | 430 | 580 | 850 |
| Rated operational current (A) | 380/400V | AC-3 AC-4 | 300 | 410 | 475 | 620 |
|  |  |  | 124 | 150 | 185 | 188 |
|  | 660/690V | AC-3 AC-4 | 190 | 235 | 290 | 360 |
|  |  |  | 60 | 72 | 85 | 170 |
| Rated insulation voltage (V AC) |  |  | 690 | 690 | 690 | 690 |
| Power of controlled 3-phase cage motor (AC-3) | kW | 380/415V AC 660/690V AC | 160 | 200 | 250 | 335 |
|  |  |  | 220 | 280 | 330 | 450 |
| AC coil(V) |  |  | 110, 127，220，240，380，415，440，480，500，600 |  |  |  |

3.ACCESSORIES