DAB7N-40 series DPN Miniature Circuit breaker(MCB)
>> Introduction
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	DAB7N-40 Series miniature circuit breaker adopts double-break point of 1P+N,the two poles are insulated and isolated from each other,under synchronous operation,N-pole always will make first and break later, which guarantees electric arc breaking capacity of protected pole, also ensures safety of controlled circuits and electric equipment.


>> Advantages
·  Two types of overcurrent protection – thermal and electromagnetic.
·  Independent contact position indicator.
·  DIN rail latch with a double fixed position.
·  Wide range of operating temperatures from –40 to +50° С.
·  Wide engagement lever with improved contact area.
·  Notches on terminal clamps lower thermal losses and boost the mechanical stability of connection.
>> Electrical parameters of DAB7N-40 miniature circuit breaker
Standard of conformity: IEC60898, GB10963
Rated power: 50-60HZ
Rated voltage: 230V
Rated current: 40A
Rated insulation voltage: 500V
Impulse withstand voltage: 4KV
Endurance: no less than 180,000 times of on-off
Instantaneous trip type: B/C
Rated breaking capacity: 6
Release type: thermo-magnetic
>> Mechanical parameters of DAB7N-40 miniature circuit breaker
Protection grade: IP20
Electric wire: 1~35mm2
Working temperature: -5~+40℃
Flame retardant grade: grade2
Altitude: ≤2000
Class of pollution: 2
Installation environment: Avoid obvious shock and vibration
Installation grade: grade II
Installation method: Using 35mm guide rail according to IEC standard
Terminal type: Dual-purpose terminal can be connected to the bus bar and conductor.
Terminal connection ability: conductor 1-25mm2, bus bar thickness 0.8-2mm
Guide rail: DIN35guide rail
>> Technical Features
	MCB DAB7-40

	For protection of general power distribution (IEC/EN 60898-1)
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	Poles
	1P

	Electrical performance

	Functions
	short circuit protection,overload protection,isolationg,control

	Rated frequency f（Hz）
	50-60Hz

	Rated working voltage Ue（V）AC
	230

	Rated current In ( A)
	40

	Rated insulated voltage Ui( V)
	500

	Impulse withstand voltage Uimp(kV)
	4

	Instantaneous tripping type
	B/C

	Rated short circuit Icn(kA)                       
	DAB7-40
	6

	Release type
	Thermal magnetic type

	Service life(O~C)
	Mechanical
	 Actual value
	12000

	
	
	 Standard value
	4000

	
	Electrical
	 Actual value
	6000

	
	
	 Standard value
	4000

	Connection and installation

	Protectiom degree
	IP20

	Wire                                            mm²
	1~35

	Working temperature
	-5～+40℃

	Resistance to humidity and heat
	Class 2

	Altitude above sea
	≤2000

	Relative humidity
	+20℃,≤90% ;+40℃,≤50%

	Pollution degree
	2

	Installation environment
	Avoid obvious shock and vibration

	Installation class
	ClassⅡ, ClassⅢ

	Mounting
	DIN35 rail

	Combination with accessories

	Auxiliary contact
	Yes

	Alarm contact
	Yes

	Shunt release
	Yes

	Undervoltage release
	Yes

	Auxiliary contact+Alarm contact
	Yes

	Dimensions(mm)  (WxHxL)         
	a
	18

	
	b
	80.7

	
	c
	72


