Applicable scope

The DAM3PV series moulded case circuit breaker is suitable for DC power grid circuit and solar photovoltaic system with maximum rated voltage of DC1500V and rated current of 800A. It has overload and short circuit protection function,used to distribute electrical energy and protect circuit and power equipment from overload, short circuit and other faults.

Normal working condition

◎Ambient air temperature

◎The upper limit of ambient air temperature is +40°C

◎The lower limit of ambient air temperatureis -5°C

◎The average temperature of the surrounding air within 24 hours shall not exceed +35°C

◎Altitude: The altitude of the installation site shall not exceed 2000m

◎The relative humidity of the atmosphere does not exceed 50% when the ambient air temperature is +40°C. At lower temperature,there can be higher relative humidity. The average maximum humidity in the wettest month is 90%, and the average minimum temperature in that monthis +25°C, and the condensation on the product surface due to temperature change should be considered.

◎Pollution level: 3

Usage and maintenance

The various characteristics and accessories of the circuit breaker are set by the manufacturer and cannot be adjusted arbitrarily during use. Under the conditions ofuser’S compliance with storage and usage, the circuit breaker seal shall be intact within 24 months from the date of shipment from the manufacturer. If the product is damaged or cannot be used normally due to manufacturing quality problem, the manufacturer shall be responsible for free replacement and repair.

Main technical parameter                                                                   Table 2

| Rated frame current Inm (A) | 250 |  |  | 250 |  | 320 |  | 400 |  |  | 630 |  | 800 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Model | DAM3PV -250 |  |  | DAM3PV -250HU |  | DAM3PV -320HU |  | DAM3PV -400HU |  |  | DAM3PV -630HU |  | DAM3PV -800HU |  |  |
| Rated current In (A) | 100A、125A、 140A、160A、 180A、200A、 225A、 250A |  |  | 125A、 140A、 160A、 180A、 200A.、225A、 250A |  | 280A、 315A、 320A |  | 225A、250A、 315A、350A、 400A |  |  | 400A、500A、 630A |  | 630A、700A、 800A |  |  |
| Number of poles | 2 | 3 | 4 | 2 | 3 | 2 | 3 | 4 |  |  | 4 |  | 4 |  |  |
| Rated working voltage Ue (V) DC | 500 | 750 | 1000 | 1000 | 1500 | 1000 | 1500 | 1000 | 1250 | 1500 | 1000 | 1500 | 1000 | 1250 | 1500 |
| Rated insulation voltage Ui (V) | 1250 |  |  | 1250 | 1500 | 1250 | 1500 | 1500 |  |  | 1500 |  | 1500 |  |  |
| Rated impulse withstand voltage Uimp(kV) | 12 |  |  | 8 | 12 | 8 | 12 | 12 |  |  | 12 |  | 12 |  |  |
| Ultimate short-circuit breaking capacity icu (kA) | 40 |  |  | 20 | 20 | 20 | 20 | 20 |  |  | 20 |  | 20 |  |  |
| Service short-circuit breaking capacity Ics (kA) | 20 |  |  | 20 | 20 | 20 | 20 | 20 |  |  | 20 |  | 20 |  |  |
| Wiring method | See attached diagram |  |  | See attached diagram |  | See attached diagram |  | See attached diagram |  |  | See attached diagram |  | See attached diagram |  |  |
| Installation method | Fixed and plug-in |  |  | Fixed and plug-in |  | Fixed and plug-in |  | Fixed and plug-in |  |  | Fixed and plug-in |  | Fixed and plug-in |  |  |
| Mechanical life (total number of times) | 8000 |  |  | 8000 |  | 8000 |  | 5000 |  |  | 5000 |  | 3000 |  |  |
| Electrical life (total number of times) | 1000 |  |  | 1000 |  | 1000 |  | 1000 |  |  | 1000 |  | 1000 |  |  |
| With isolation characteristic or not | Yes |  |  | Yes |  | Yes |  | Yes |  |  | Yes |  | Yes |  |  |
| Allowable usage ambient temperature ("C) | -5℃~+40℃ |  |  | -5℃~+40℃ |  | -5℃~+40℃ |  | -5℃~+40℃ |  |  | -5℃~+40℃ |  | -5℃~+40℃ |  |  |
| Protection level | IP20 |  |  | IP20 |  | IP20 |  | IP20 |  |  | IP20 |  | IP20 |  |  |
| Accessory attachable | Auxiliary,shunt, alarm,manual operation, electric operation |  |  | Auxiliary,shunt. alarm,manual operation, electric operation |  | Auxiliary,shunt, alarm, manual operation, electric operation" |  | Auxiliary,shunt, alarm,manual operation, electric operation |  |  | Auxiliary,shunt, alarm, manual operation, electric operation |  | Auxiliary,shunt, alarm,manual operation, electric operation |  |  |
| Instantaneous action value | 10in |  |  | 10In |  | 10ln |  | 10in |  |  | 10in |  | 10in |  |  |
| Arc distance (mm) | ≤50 |  |  | ≤50(0 with cover) |  | ≤50 (0 with cover) |  | ≤50 (0 with cover) |  |  | ≤50 (0 with cover) |  | ≤50(0 with cover) |  |  |
| Outline dimension (L×W×H)(mm) | 2P:165×72×127 3P:165x107x127 4P:165×142×127 |  |  | 2P:180×76×126 3P:180x107x126 |  | 2P:180×76×126 3P:180x107x126 |  | 258×200×107 |  |  | 280×280×116 |  | 280×280×116 |  |  |

Wiring method: DC product wiring diagram

Circuit breaker action characteristic curve

M3- (HU) action characteristic curve              DAM3PV action characteristic curve

Safety distance during circuit breaker installation

| Model | L | A |  | B | C | E |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | With zero arc cover | Without zero arc cover |  |  | With zero arc cover | Without zero arc cover |
| DAM3PV-250/320HU | 40 | 50 | 30 | 25 | 25 | 60 | 60 |
| DAM3PV-400HU |  | 50 | 30 | 25 | 25 | 60 | 60 |
| DAM3PV-800HU | 70 | 100 | 30 | 25 | 25 | 100 | 60 |
|  | In the figure: 1. No insulation connection; 2 insulated wires; 3 cable terminal |  |  |  |  |  |  |

Release method and accessory code

Classification by release type: only instantaneous release (electromagnetic release:200); Thermal+electromagnetic release

(complex type: 300)

Outline and installation dimension

DAM3PV-250 outline and installation dimension

| Outline dimension |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Installation dimension |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| C | E | F | G | G1 | H | H1 | H2 | H3 | H4 | し | L1 | L2 | W | W1 | W2 | W3 | A | B | d |
| 102 | 50 | 22 | 23 | 11.5 | 103 | 127 | 23 | 4 | 5 | 165(171 with protective cover) | 360 | 144 | 107 | 35 | 142 | 72 | 35 | 126 | φ5 |

DAM3PV-250/320HU outline and installation dimension

DAM3PV-400HU outline and installation dimension

M3(DC) -400 outline and installation dimension (except for M3-400HU)

DAM3PV-630/800HU outline and installation dimension

Installation diagram of DAM3PV with arc cover

| Model | Arc cover length A | Total length B |
| --- | --- | --- |
| DAM3PV-250/320HU | 69 | 234 |
| DAM3PV-400HU | 72 | 330 |
| DAM3PV-630/800HU | 67.5 | 347.5 |